{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":48,"n_cols":12,"rows_kept":48,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FBA-A(9)"]
[]
[]
[]
[]
["","","","","","FBA35A2VEB9","FBA50A2VEB9","FBA60A2VEB9","FBA71A2VEB9","FBA100A2VEB","FBA125A2VEB","FBA140A2VEB"]
["Cooling capacity","Total capacity","","Nom.","كيلو واط","","","","","","14.00","15.40"]
["استطاعة التدفئة","الاستطاعة الإجمالية","","الإسمي","كيلو واط","","","","","","13.5","15.5"]
["الغلاف","اللون","","","","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)","Not painted (galvanised)"]
["","المادة","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["الأبعاد","الوحدة","","الارتفاع","mm","245","245","245","245","245","245","245"]
["","","","العرض","mm","700","700","1000","1000","1400","1400","1400"]
["","","","العمق","mm","800","800","800","800","800","800","800"]
["الوزن","الوحدة","","","كغ","28.0","28.0","35.0","35.0","46.0","46.0","46.0"]
["Fan","Air flow rate","التبريد","High","م³/دقيقة","15.0","15.0","18.0","18.0","29.0","34.0","34.0"]
["مروحة","معدل تدفق الهواء","تبريد","متوسط","م³/دقيقة","12.5","12.5","15.0","15.0","24.5","29.0","29.0"]
["Fan","Air flow rate","التبريد","Low","م³/دقيقة","10.5","10.5","12.5","12.5","20.0","23.5","23.5"]
["","","التدفئة","High","م³/دقيقة","15.0","15.0","18.0","18.0","29.0","34.0","34.0"]
["مروحة","معدل تدفق الهواء","تدفئة","متوسط","م³/دقيقة","12.5","12.5","15.0","15.0","24.5","29.0","29.0"]
["Fan","Air flow rate","التدفئة","Low","م³/دقيقة","10.5","10.5","12.5","12.5","20.0","23.5","23.5"]
["مروحة","الضغط الاستاتيكي الخارجي","","الإسمي","باسكال","30","30","30","30","40","50","50"]
["مستوى طاقة الصوت","التبريد","","","ديسيبل أمبير","60.0","60.0","56.0","56.0","58.0","62.0","62.0"]
["Sound pressure level","Cooling","","High","ديسيبل أمبير","35.0","35.0","30.0","30.0","34.0","37.0","37.0"]
["مستوى ضغط الصوت","تبريد","","متوسط","ديسيبل أمبير","32.0","32.0","28.0","28.0","32.0","35.0","35.0"]
["Sound pressure level","Cooling","","Low","ديسيبل أمبير","29.0","29.0","25.0","25.0","30.0","32.0","32.0"]
["","Heating","","High","ديسيبل أمبير","37.0","37.0","31.0","31.0","36.0","38.0","38.0"]
["مستوى ضغط الصوت","تدفئة","","متوسط","ديسيبل أمبير","34.0","34.0","28.0","28.0","33.0","35.0","35.0"]
["Sound pressure level","Heating","","Low","ديسيبل أمبير","29.0","29.0","25.0","25.0","30.0","32.0","32.0"]
["وصلات الأنابيب","سائل","","القطر الخارجي","mm","6.35","6.35","6.35","9.52","9.52","9.52","9.52"]
["","غاز","","القطر الخارجي","mm","9.52","12.70","12.70","15.90","15.90","15.90","15.90"]
["","التصريف","","","","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)","VP20 (I.D. 20/O.D. 26)"]
["ارتفاع الصرف","mm","","","","625","625","625","625","625","625","625"]
["أنظمة التحكم","جهاز تحكم عن بُعد بالأشعة تحت الحمراء","","","","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66","BRC4C65, BRC4C66"]
["","جهاز تحكم عن بُعد سلكي","","","","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52","BRC1H52W/S/K, BRC1E53A, BRC1E53B, BRC1E53C, BRC1D52"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1"]
["","Washer for hanger bracket","","","","8","8","8","8","8","8","8"]
["","Operation manual","","","","1","1","1","1","1","1","1"]
["","Clamps","","","","4","4","4","4","4","4","4"]
["","Drain hose","","","","1","1","1","1","1","1","1"]
["","Insulation for fitting","","","","2","2","2","2","2","2","2"]
["","Metal clamp for drain hose","","","","1","1","1","1","1","1","1"]
["","Screws","","","","40","40","40","40","40","40","40"]
["","Sealing pads","","","","5","5","5","5","5","5","5"]
["وحدة التزويد بالطاقة","الطور","","","","1~","1~","1~","1~","1~","1~","1~"]
["Power supply","Frequency","","","هرتز","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","","","","","","(1) - مستوى قوة الصوت هو قيمة مطلقة تشير إلى الطاقة التي يولدها مصدر الصوت."]
["","","","","","","","","","","(2) - انظر المخطط المنفصل الخاص بالبيانات الكهربائية"]