{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":116,"n_cols":12,"rows_kept":116,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWE-CT"]
[]
[]
[]
[]
["","","","","","FWE02CT","FWE03CT","FWE04CT","FWE06CT","FWE07CT","FWE08CT","FWE10CT"]
["Sound pressure level","Fan speed 1","","","dBA","21.0 (6)","","","","40.0 (6)"]
["","Low","","","dBA","31.0 (6)","","","","40.0 (6)"]
["","High","","","dBA","45.0 (6)","","","","55.0 (6)"]
["Total sound power level","Low","","","dBA","41.0 (5)","","","","50.0 (5)"]
["","Fan speed 1","","","dBA","31.0 (5)","","","","50.0 (5)"]
["","High","","","dBA","55.0 (5)","","","","65.0 (5)"]
["Water flow","Cooling","","Low","l/h","263 (1)","","","","813 (1)"]
["","","","Fan speed 1","l/h","241 (1)","","","","689 (1)"]
["","","","High","l/h","357 (1)","","","","1,119 (1)"]
["","Heating","","Fan speed 1","l/h","276 (2)","","","","824 (2)"]
["","","","High","l/h","422 (2)","","","","1,415 (2)"]
["","","","Low","l/h","304 (2)","","","","992 (2)"]
["","Water pressure drop","Heating","Fan speed 1","kPa","13.00 (2)","","","","12.00 (2)"]
["","","","High","kPa","18.89 (2)","","","","19.20 (2)"]
["","","","Low","kPa","13.65 (2)","","","","13.51 (2)"]
["","","Cooling","High","kPa","11.74 (2)","","","","10.79 (2)"]
["","","","Fan speed 1","kPa","6.00 (2)","","","","5.00 (2)"]
["","","","Low","kPa","7.30 (2)","","","","6.60 (2)"]
["Piping connections","Drain","","OD","mm","R 3/4\"","","","","R 3/4\""]
["","Water","","Inlet","","3/4\"","","","","3/4\""]
["","","","Outlet","","3/4\"","","","","3/4\""]
["Power input","Fan speed 1","","","kW","0.030 (4)","","","","0.090 (4)"]
["","High","","","kW","0.046 (4)","","","","0.163 (4)"]
["","Low","","","kW","0.034 (4)","","","","0.105 (4)"]
["Allowed water temperature","Heating","","Max.","°C","70.000","","","","70.000"]
["","","","Min.","°C","3.00","","","","3.00"]
["","Cooling","","Min.","°C","3","","","","3"]
["","","","Max.","°C","70.0","","","","70.0"]
["Dimensions","Unit","","Width","mm","590","","","","590"]
["","","","Depth","mm","705","","","","1,460"]
["","","","Height","mm","253","","","","253"]
["Casing","Colour","","","","Metal","","","","Metal"]
["Weight","Unit","","","kg","17.0","","","","36.7"]
["Fan","Air flow rate","","Fan speed 1","m³/h","193 (4)","","","","569 (4)"]
["","","","Low","m³/h","238 (4)","","","","851 (4)"]
["","","","High","m³/h","430 (4)","","","","1,559 (4)"]
["","Available static pressure","","Fan speed 1","Pa","4","","","","30"]
["","","","High","Pa","33","","","","67"]
["","","","Low","Pa","18","","","","48"]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Low","kW","1.13 (1)","","","","3.61 (1)"]
["","","","Fan speed 1","kW","1.04 (1)","","","","2.97 (1)"]
["","","","High","kW","1.56 (1)","","","","4.67 (1)"]
["","Total capacity 2-pipe","","Low","kW","1.57 (1)","","","","4.84 (1)"]
["","","","High","kW","2.12 (1)","","","","6.67 (1)"]
["","","","Fan speed 1","kW","1.40 (1)","","","","4.01 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","High","kW","2.38 (2)","","","","7.96 (2)"]
["","","","Low","kW","1.72 (2)","","","","5.62 (2)"]
["","","","Fan speed 1","kW","1.60 (2)","","","","4.79 (2)"]
["Current input","High","","","A","0.206","","","","0.731"]
["","Low","","","A","0.150","","","","0.472"]
["","Fan speed 1","","","A","0.128","","","","0.400"]
["Power supply","Type","","","","220-240 / 1 / 50","","","","220-240 / 1 / 50"]
["","Phase","","","","1~","","","","1~"]
["","Frequency","","","Hz","50","","","","50"]
["","Voltage","","","V","220-240","","","","220-240"]
["Notes","","","","","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB","(1) - Inlet/outlet water temperature 7/12 °C; inlet air temperature 27°C DB 19°C WB"]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(3) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(3) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(3) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition."]
["","","","","","(4) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Airflow value measurements are performed at 20C (DB) /15 C(WB) condition.","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - Sound power level according to ISO3741","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - Sound power level according to ISO3741","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(5) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["","","","","","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","","","","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit."]
["Cooling capacity (standard conditions)","Sensible capacity 2-pipe","","Fan speed 1","kW","","1.55 (1)","1.79 (1)","3.16 (1)","","3.78 (1)","4.78 (1)"]
["","","","Low","kW","","1.77 (1)","2.11 (1)","3.32 (1)","","4.44 (1)","5.46 (1)"]
["","","","High","kW","","2.37 (1)","3.19 (1)","4.404 (1)","","5.84 (1)","7.19 (1)"]
["","Total capacity 2-pipe","","Fan speed 1","kW","","2.09 (1)","2.42 (1)","3.912 (1)","","5.10 (1)","6.45 (1)"]
["","","","Low","kW","","2.40 (1)","2.73 (1)","4.48 (1)","","5.95 (1)","7.37 (1)"]
["","","","High","kW","","3.15 (1)","4.00 (1)","5.94 (1)","","7.66 (1)","9.71 (1)"]
["Heating capacity (standard conditions)","Capacity 2-pipe","","Fan speed 1","kW","","2.48 (2)","2.49 (2)","4.13 (2)","","4.88 (2)","7.19 (2)"]
["","","","Low","kW","","2.74 (2)","2.81 (2)","4.40 (2)","","6.07 (2)","8.28 (2)"]
["","","","High","kW","","3.66 (2)","4.77 (2)","6.09 (2)","","9.11 (2)","11.46 (2)"]
["Power input","Fan speed 1","","","kW","","0.040 (4)","0.040 (4)","0.060 (4)","","0.100 (4)","0.120 (4)"]
["","Low","","","kW","","0.047 (4)","0.050 (4)","0.081 (4)","","0.133 (4)","0.145 (4)"]
["","High","","","kW","","0.069 (4)","0.083 (4)","0.119 (4)","","0.181 (4)","0.230 (4)"]
["Dimensions","Unit","","Height","mm","","253","253","253","","253","253"]
["","","","Width","mm","","590","590","590","","590","590"]
["","","","Depth","mm","","875","1010","1210","","1560","1820"]
["Weight","Unit","","","kg","","20.2","23.7","28.4","","39.1","45.5"]
["Casing","Colour","","","","","Metal","Metal","Metal","","Metal","Metal"]
["Fan","Air flow rate","","Fan speed 1","m³/h","","295 (4)","310 (4)","540 (4)","","688 (4)","870 (4)"]
["","","","Low","m³/h","","385 (4)","413 (4)","630 (4)","","1016 (4)","1202 (4)"]
["","","","High","m³/h","","638 (4)","910 (4)","1195 (4)","","1753 (4)","2177 (4)"]
["","Available static pressure","","Fan speed 1","Pa","","7","7","4","","30","30"]
["","","","Low","Pa","","35","38","45","","48","48"]
["","","","High","Pa","","63","63","65","","67","70"]
["Total sound power level","Fan speed 1","","","dBA","","38.0 (5)","32.0 (5)","39.0 (5)","","46.0 (5)","46.0 (5)"]
["","Low","","","dBA","","49.0 (5)","40.0 (5)","48.0 (5)","","54.0 (5)","50.0 (5)"]
["","High","","","dBA","","61.0 (5)","58.0 (5)","62.0 (5)","","64.0 (5)","65.0 (5)"]
["Sound pressure level","Fan speed 1","","","dBA","","28.0 (6)","22.0 (6)","29.0 (6)","","36.0 (6)","36.0 (6)"]
["","Low","","","dBA","","39.0 (6)","30.0 (6)","38.0 (6)","","44.0 (6)","40.0 (6)"]
["","High","","","dBA","","51.0 (6)","48.0 (6)","52.0 (6)","","54.0 (6)","55.0 (6)"]
["Water flow","Cooling","","Fan speed 1","l/h","","359 (1)","416 (1)","683 (1)","","877 (1)","1110 (1)"]
["","","","Low","l/h","","404 (1)","460 (1)","721 (1)","","1001 (1)","1242 (1)"]
["","","","High","l/h","","531 (1)","677 (1)","958 (1)","","1284 (1)","1630 (1)"]
["","Heating","","Fan speed 1","l/h","","426 (2)","429 (2)","710 (2)","","839 (2)","1237 (2)"]
["","","","Low","l/h","","484 (2)","502 (2)","756 (2)","","1082 (2)","1423 (2)"]
["","","","High","l/h","","649 (2)","852 (2)","1047 (2)","","1629 (2)","1970 (2)"]
["","Water pressure drop","Cooling","Fan speed 1","kPa","","13.00 (2)","9.00 (2)","20.79 (2)","","9.00 (2)","14.00 (2)"]
["","","","Low","kPa","","16.87 (2)","11.28 (2)","23.15 (2)","","10.94 (2)","17.59 (2)"]
["","","","High","kPa","","27.39 (2)","24.51 (2)","40.85 (2)","","16.10 (2)","28.31 (2)"]
["","","Heating","Fan speed 1","kPa","","23.00 (2)","14.00 (2)","23.61 (2)","","12.00 (2)","17.00 (2)"]
["","","","Low","kPa","","26.83 (2)","15.65 (2)","26.21 (2)","","15.44 (2)","20.42 (2)"]
["","","","High","kPa","","39.79 (2)","30.09 (2)","45.52 (2)","","24.85 (2)","34.55 (2)"]
["Allowed water temperature","Cooling","","Min.","°C","","3","3","3","","3","3"]
["","","","Max.","°C","","70.0","70.0","70.0","","70.0","70.0"]
["","Heating","","Min.","°C","","3.00","3.00","3.00","","3.00","3.00"]
["","","","Max.","°C","","70.000","70.000","70.000","","70.000","70.000"]
["Power supply","Frequency","","","Hz","","50","50","50","","50","50"]
["Current input","Fan speed 1","","","A","","0.177","0.188","0.271","","0.456","0.540"]
["","Low","","","A","","0.208","0.217","0.325","","0.523","0.648"]
["","High","","","A","","0.309","0.372","0.533","","0.811","1.031"]