{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":66,"n_cols":17,"rows_kept":66,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWM-DAF"]
[]
[]
[]
[]
["","","","","","FWM01DAFV3","FWM15DAFV3","FWM15DAFVS","FWM02DAFVS","FWM25DAFV3","FWM25DAFVS","FWM03DAFV3","FWM04DAFV3","FWM04DAFVS","FWM06DAFV3","FWM06DAFVS","FWM10DAFV3"]
["Sound pressure level","Fan speed 1","","","dBA","","","27 (6)","27 (6)","","21 (6)","","","32 (6)","","34 (6)"]
["","Low","","","dBA","28 (6)","33 (6)","","","29 (6)","","28 (6)","32 (6)","","43 (6)","","43 (6)"]
["","Fan speed 6","","","dBA","","","50 (6)","50 (6)","","47 (6)","","","55 (6)","","55 (6)"]
["","High","","","dBA","40 (6)","44 (6)","","","43 (6)","","42 (6)","51 (6)","","54 (6)","","61 (6)"]
["Total sound power level","Low","","","dBA","33 (4)","40 (4)","","","34 (4)","","33 (4)","39 (4)","","48 (4)","","48 (4)"]
["","Fan speed 1","","","dBA","","","32 (4)","32 (4)","","26 (4)","","","39 (4)","","39 (4)"]
["","Fan speed 6","","","dBA","","","55 (4)","55 (4)","","52 (4)","","","60 (4)","","60 (4)"]
["","High","","","dBA","45 (4)","49 (4)","","","48 (4)","","47 (4)","56 (4)","","58 (4)","","66 (4)"]
["Water flow","Cooling","","Low","l/h","169 (1)","212 (1)","","","272 (1)","","297 (1)","425 (1)","","535 (1)","","699 (1)"]
["","","","Fan speed 1","l/h","","","174 (1)","209 (1)","","245 (1)","","","425 (1)","","457 (1)"]
["","","","Fan speed 6","l/h","","","241 (1)","403 (1)","","498 (1)","","","902 (1)","","915 (1)"]
["","","","High","l/h","250 (1)","291 (1)","","","409 (1)","","493 (1)","730 (1)","","802 (1)","","1,352 (1)"]
["","Heating","","Fan speed 1","l/h","","","119 (3)","117 (3)","","145 (3)","","","277 (3)","","282 (3)"]
["","","","Fan speed 6","l/h","","","175 (3)","175 (3)","","267 (3)","","","441 (3)","","441 (3)"]
["","","","High","l/h","146 (3)","154 (3)","","","222 (3)","","234 (3)","334 (3)","","406 (3)","","643 (3)"]
["","","","Low","l/h","115 (3)","120 (3)","","","156 (3)","","165 (3)","238 (3)","","311 (3)","","425 (3)"]
["","Water pressure drop","Heating","Fan speed 1","kPa","","","4 (3)","4 (3)","","2 (3)","","","6 (3)","","4 (3)"]
["","","","High","kPa","4 (3)","7 (3)","","","3 (3)","","4 (3)","14 (3)","","8 (3)","","29 (3)"]
["","","","Fan speed 6","kPa","","","8 (3)","7 (3)","","5 (3)","","","12 (3)","","9 (3)"]
["","","","Low","kPa","3 (3)","4 (3)","","","2 (3)","","2 (3)","8 (3)","","5 (3)","","14 (3)"]
["","","Cooling","Fan speed 6","kPa","","","10 (1)","21 (1)","","22 (1)","","","17 (1)","","17 (1)"]
["","","","High","kPa","12 (1)","14 (1)","","","16 (1)","","11 (1)","12 (1)","","14 (1)","","16 (1)"]
["","","","Fan speed 1","kPa","","","6 (1)","7 (1)","","6 (1)","","","5 (1)","","5 (1)"]
["","","","Low","kPa","6 (1)","8 (1)","","","8 (1)","","5 (1)","5 (1)","","7 (1)","","5 (1)"]
["Piping connections","Drain","","OD","mm","16","16","16","16","16","16","16","16","16","16","16","16"]
["Power input","Fan speed 6","","","kW","","","0.066","0.066","","0.082","","","0.105","","0.105"]
["","Fan speed 1","","","kW","","","0.02","0.02","","0.02","","","0.04","","0.04"]
["","High","","","kW","0.037","0.053","","","0.057","","0.056","0.098","","0.098","","0.244"]
["","Low","","","kW","0.02","0.03","","","0.03","","0.03","0.04","","0.05","","0.11"]
["Dimensions","Unit","","Width","mm","584","584","584","584","794","794","794","1,000","1,000","1,000","1,000","1,210"]
["","","","Depth","mm","224","224","224","224","224","224","224","224","224","224","224","249"]
["","","","Height","mm","535","535","535","535","535","535","535","535","535","535","535","535"]
["Water connections","Additional coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\""]
["","Primary coil","","","inch","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","1/2\"","3/4 \""]
["Weight","Unit","","","kg","16.5","16.5","16.5","16.9","21.4","21.4","22.1","26.4","26.4","26.6","26.6","35.4"]
["Cooling capacity (standard conditions)","Total capacity 4-pipe","","Fan speed 6","kW","","","1.33 (1)","2.28 (1)","","2.82 (1)","","","5.16 (1)","","5.23 (1)"]
["","","","Fan speed 1","kW","","","1.00 (1)","1.20 (1)","","1.41 (1)","","","2.44 (1)","","2.63 (1)"]
["","","","Low","kW","0.97 (1)","1.22 (1)","","","1.55 (1)","","1.70 (1)","2.44 (1)","","3.06 (1)","","3.96 (1)"]
["","","","High","kW","1.42 (1)","1.64 (1)","","","2.32 (1)","","2.81 (1)","4.16 (1)","","4.57 (1)","","7.64 (1)"]
["","Sensible capacity 4-pipe","","Low","kW","0.73 (1)","0.91 (1)","","","1.14 (1)","","1.21 (1)","1.74 (1)","","2.23 (1)","","2.91 (1)"]
["","","","Fan speed 1","kW","","","0.84 (1)","0.92 (1)","","1.03 (1)","","","1.74 (1)","","1.92 (1)"]
["","","","High","kW","1.10 (1)","1.22 (1)","","","1.79 (1)","","2.01 (1)","2.99 (1)","","3.47 (1)","","5.61 (1)"]
["Heating capacity (standard conditions)","Capacity 4-pipe","","Fan speed 6","kW","","","2.00 (3)","2.00 (3)","","3.06 (3)","","","5.04 (3)","","5.04 (3)"]
["","","","Low","kW","1.31 (3)","1.36 (3)","","","1.78 (3)","","1.88 (3)","2.73 (3)","","3.55 (3)","","4.85 (3)"]
["","","","Fan speed 1","kW","","","1.36 (3)","1.33 (3)","","1.66 (3)","","","2.73 (3)","","3.23 (3)"]
["","","","High","kW","1.66 (3)","1.76 (3)","","","2.53 (3)","","2.68 (3)","3.82 (3)","","4.64 (3)","","7.35 (3)"]
["Current input","High","","","A","0.16","0.20","","","0.27","","0.27","0.40","","0.39","","1.07"]
["","Fan speed 6","","","A","","","0.29","0.29","","0.36","","","0.47","","0.47"]
["","Low","","","A","0.09","0.11","","","0.14","","0.14","0.19","","0.19","","0.54"]
["","Fan speed 1","","","A","","","0.08","0.08","","0.11","","","0.19","","0.19"]
["Power supply","Type","","","","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50","230 /  1 /  50"]
["","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","230","230","230","230","230","230","230","230","230","230","230","230"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; entering water temp. 7°C, water temperature rise 5K."]
["","","","","","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K.","(2) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 45°C, water temperature drop 5K."]
["","","","","","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K.","(3) - Heating: indoor temp. 20°CDB, 15°CWB; entering water temp. 65°C, water temperature drop 10K."]
["","","","","","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741","(4) - Sound power level according to ISO3741"]
["","","","","","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting","(5) - SL: The silent fan level of the air flow rate setting"]
["","","","","","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit.","(6) - The sound pressure level is measured via a microphone at 1m distance of the unit."]