{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":64,"n_cols":15,"rows_kept":64,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FXMQ-P"]
[]
[]
[]
[]
["","","","","","FXMQ20PVE","FXMQ25PVE","FXMQ32PVE","FXMQ40PVE","FXMQ50PVE","FXMQ63PVE","FXMQ80PVE","FXMQ100PVE","FXMQ125PVE","FXMQ140PVE"]
["Sound pressure level","Cooling","","At low fan speed","dBA","","","","","","","","","","43"]
["","","","At high fan speed","dBA","","","","","","","","","","45"]
["","","","Super high","dBA","33","33","34","39","41","42","43","43","44","46"]
["Standard Accessories","Operation manual","","","","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual","Operation manual"]
["","Installation manual","","","","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual","Installation manual"]
["","Drain hose","","","","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose","Drain hose"]
["","Sealing pads","","","","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads","Sealing pads"]
["","Clamps","","","","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps","Clamps"]
["","Washer","","","","Washer","Washer","Washer","Washer","Washer","Washer","Washer","Washer","Washer","Washer"]
["","Screws","","","","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws","Screws"]
["","Insulation for fitting","","","","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting","Insulation for fitting"]
["","Clamp metal","","","","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal","Clamp metal"]
["","Air discharge flange","","","","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange","Air discharge flange"]
["","Air suction flange","","","","Air suction flange","Air suction flange","Air suction flange","Air suction flange","Air suction flange","Air suction flange","Air suction flange","Air suction flange","Air suction flange","Air suction flange"]
["System","Connectable outdoor unit system","","","","","","","","","","","","","R410A VRV Series"]
["Power input - 50Hz","Cooling","","At high fan speed","kW","","","","","","","","","","0.461"]
["","Heating","","At high fan speed","kW","","","","","","","","","","0.449"]
["Cooling capacity","Total capacity","","At high fan speed","kW","","","","","","","","","","16.0 (1)"]
["Piping connections","Liquid","","OD","mm","6.35","6.35","6.35","6.35","6.35","9.52","9.52","9.52","9.52","9.52"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Gas","","OD","mm","12.7","12.7","12.7","12.7","12.7","15.9","15.9","15.9","15.9","15.9"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Drain","","","","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)","VP25 (O.D. 32 / I.D. 25)"]
["Dimensions","Unit","","Width","mm","550","550","550","700","1,000","1,000","1,000","1,400","1,400","1,400"]
["","","","Depth","mm","700","700","700","700","700","700","700","700","700","700"]
["","","","Height","mm","300","300","300","300","300","300","300","300","300","300"]
["Casing","Material","","","","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate","Galvanised steel plate"]
["Weight","Unit","","","kg","25","25","25","28","36","36","36","46","46","47"]
["Fan","External static pressure - 50Hz","","High","Pa","100","100","100","160","200","200","200","200","200","140"]
["","","","Low","Pa","30","30","30","30","50","50","50","50","50","50"]
["","External static pressure - 60Hz","","High","Pa","100","100","100","160","200","200","200","200","200","140"]
["","","","Low","Pa","30","30","30","30","50","50","50","50","50","50"]
["","Air flow rate - 50Hz","Cooling","At high fan speed","m³/min","","","","","","","","","","39"]
["","","","At low fan speed","m³/min","","","","","","","","","","32"]
["","","","Super high","m³/min","","","","","","","","","","46"]
["","Air flow rate - 60Hz","Cooling","High","m³/min","","","","","","","","","","39"]
["","","","Super high","m³/min","","","","","","","","","","46"]
["","","","Low","m³/min","","","","","","","","","","32"]
["Heating capacity","Total capacity","","At high fan speed","kW","","","","","","","","","","18.0 (2)"]
["Current - 50Hz","Maximum fuse amps (MFA)","","","A","16","16","16","16","16","16","16","16","16","16"]
["Power supply","Phase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Name","","","","VE","VE","VE","VE","VE","VE","VE","VE","VE","VE"]
["","Frequency","","","Hz","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60","50/60"]
["","Voltage","","","V","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220","220-240/220"]
["Notes","","","","","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(1) - Cooling: return air temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)","(2) - Heating: return air temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; standard external static pressure; equivalent refrigerant piping: 7.5m (horizontal)"]
["","","","","","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat.","(3) - Capacities are net, including a deduction for cooling (an addition for heating) for indoor fan motor heat."]
["","","","","","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control.","(4) - External static pressure is changeable in 7 stages (20, 25, 32 class); 13 stages (40 class); 14 stages (50, 63, 80, 100, 125 class); 10 stages (140 class) within the range of the remote control."]
["","","","","","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - The air filter is not a standard accessory, but please mount it in the duct system of the suction side. Select its colorimetric method (gravity method) 50% or more.","(5) - Air filter is not standard accessory, but please mount it in the duct system of the suction side. Select its dust collection efficiency (gravity method) 50% and more."]
["","","","","","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(6) - Operation sound differs with operation and ambient conditions"]
["","","","","","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Maximum allowable voltage range variation between phases is 2%.","(7) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - MCA/MFA: MCA = 1.25 x FLA","(8) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MFA ≤ 4 x FLA","(9) - MCA/MFA: MCA = 1.25 x FLA"]
["","","","","","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - Next lower standard fuse rating minimum 16A","(10) - MFA ≤ 4 x FLA"]
["","","","","","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Next lower standard fuse rating minimum 16A"]
["","","","","","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Instead of a fuse, use a circuit breaker","(12) - Select wire size based on the value of MCA"]
["","","","","","","","","","","","","","","(13) - Instead of a fuse, use a circuit breaker"]
["","","","","","","","","","","","","","","(14) - The above is the value when air flow rate is maximum at maximum external static pressure position."]