{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":67,"n_cols":14,"rows_kept":67,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RWEYQ-P"]
[]
[]
[]
[]
["","","","","","RWEYQ8PY1","RWEYQ10PY1","RWEYQ16PY1","RWEYQ18PY1","RWEYQ20PY1","RWEYQ24PY1","RWEYQ26PY1","RWEYQ28PY1","RWEYQ30PY1"]
["Sound pressure level","Cooling","","Nom.","dBA","50","51","53","54","54","55","55","55","56"]
["Standard Accessories","Installation manual","","","","Installation manual","Installation manual"]
["","Operation manual","","","","Operation manual","Operation manual"]
["","Connection pipes","","","","Connection pipes","Connection pipes"]
["","Clamps","","","","Clamps","Clamps"]
["Capacity range","HP","","","","8","10","16","18","20","24","26","28","30"]
["Maximum number of connectable indoor units","","","","","17","21","34","36","36","36","36","36","36"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","149","150"]
["EER","","","","","4.89","4.14","4.92","4.63","4.41","4.91","4.74","4.57","4.43"]
["Refrigerant","Charge","","","TCO2Eq","7.3","8.8"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","3.5","4.2"]
["","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["System","Outdoor unit module 2","","","","","","RWEYQ8PY1","RWEYQ8PY1","RWEYQ10PY1","RWEYQ8PY1","RWEYQ8PY1","RWEYQ10PY1","RWEYQ10PY1"]
["","Outdoor unit module 3","","","","","","","","","RWEYQ8PY1","RWEYQ8PY1","RWEYQ8PY1","RWEYQ10PY1"]
["","Outdoor unit module 1","","","","RWEYQ8PY1","RWEYQ10PY1","RWEYQ8PY1","RWEYQ10PY1","RWEYQ10PY1","RWEYQ8PY1","RWEYQ10PY1","RWEYQ10PY1","RWEYQ10PY1"]
["Power input - 50Hz","Cooling","","Nom.","kW","4.55","6.03","9.10","10.6","12.1","13.7","15.1","16.6","18.1"]
["","Heating","","Nom.","kW","4.24","6.05","8.48","10.3","12.1","12.7","14.5","16.3","18.2"]
["Indoor index connection","Nom.","","","","200","250","400","450","500","600","650","700","750"]
["","Min.","","","","100","125","200","225","250","300","325","350","375"]
["","Max.","","","","260","325","520","585","650","780","845","910","975"]
["Cooling capacity","Nom.","","","kW","22.4 (1)","26.7 (1)","44.8 (1)","49.1 (1)","53.4 (1)","67.2 (1)","71.5 (1)","75.8 (1)","80.1 (1)"]
["Piping connections","Liquid","","OD","mm","9.52","9.52","12.7","15.9","15.9","15.9","19.1","19.1","19.1"]
["","","","Type","","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection","Flare connection"]
["","Total piping length","System","Actual","m","300","300","300","300","300","300","300","300","300"]
["","Gas","","OD","mm","19.1 (3)","22.2 (3)","28.6 (3)","28.6 (3)","28.6 (3)","34.9 (3)","34.9 (3)","34.9 (3)","34.9 (3)"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Drain","","Outlet","","PS 1/2B internal thread","PS 1/2B internal thread"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","50","50","50","50","50","50","50","50","50"]
["","","","Indoor unit in highest position","m","40","40","40","40","40","40","40","40","40"]
["","","IU - IU","Max.","m","15","15","15","15","15","15","15","15","15"]
["","Discharge gas","","OD","mm","15.9 (4), 19.1 (5)","19.1 (4), 22.2 (5)","22.2 (4), 28.6 (5)","22.2 (4), 28.6 (5)","22.2 (4), 28.6 (5)","28.6 (4), 34.9 (5)","28.6 (4), 34.9 (5)","28.6 (4), 34.9 (5)","28.6 (4), 34.9 (5)"]
["","","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Water","","Inlet","","PT1 1/4B internal thread","PT1 1/4B internal thread"]
["","","","Outlet","","PT1 1/4B internal thread","PT1 1/4B internal thread"]
["COP","","","","","5.81","5.08","5.87","5.48","5.21","5.91","5.62","5.40","5.19"]
["Dimensions","Unit","","Width","mm","780","780"]
["","","","Depth","mm","550","550"]
["","","","Height","mm","1,000","1,000"]
["Heating capacity","Nom.","","","kW","25.0 (2)","31.5 (2)","50.0 (2)","56.5 (2)","63.0 (2)","75.0 (2)","81.5 (2)","88.0 (2)","94.5 (2)"]
["Power supply","Phase","","","","3~","3~","3~","3~","3~","3~","3~","3~","3~"]
["","Name","","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m.","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; Inlet water temperature: 30°C; equivalent refrigerant piping: 7.5m; level difference: 0m."]
["","","","","","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; inlet water temperature: 20°C; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used","(3) - In case of heat pump system, gas pipe is not used"]
["","","","","","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system","(4) - In case of heat recovery system"]
["","","","","","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system","(5) - In case of heat pump system"]
["","","","","","(6) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(6) - This unit should not be installed outdoors, but indoors e.g. in a machine room.","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(6) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C"]
["","","","","","(7) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.64kW/8HP","(7) - Hold ambient temperature at 0-40°C and humidity at 80%RH or less. Heat rejection from the casing: 0.71kW/10HP","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set.","(7) - TOCA means the total value of each OC set."]
["","","","","","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(8) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; inlet water temp. 30°C","(8) - MSC means the maximum current during start up of the compressor","(8) - MSC means the maximum current during start up of the compressor","(8) - MSC means the maximum current during start up of the compressor","(8) - MSC means the maximum current during start up of the compressor","(8) - MSC means the maximum current during start up of the compressor","(8) - MSC means the maximum current during start up of the compressor","(8) - MSC means the maximum current during start up of the compressor"]
["","","","","","(9) - TOCA means the total value of each OC set.","(9) - TOCA means the total value of each OC set.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(9) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(10) - MSC means the maximum current during start up of the compressor","(10) - MSC means the maximum current during start up of the compressor","(10) - Maximum allowable voltage range variation between phases is 2%.","(10) - Maximum allowable voltage range variation between phases is 2%.","(10) - Maximum allowable voltage range variation between phases is 2%.","(10) - Maximum allowable voltage range variation between phases is 2%.","(10) - Maximum allowable voltage range variation between phases is 2%.","(10) - Maximum allowable voltage range variation between phases is 2%.","(10) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(11) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(11) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA","(11) - Select wire size based on the value of MCA"]
["","","","","","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(13) - Select wire size based on the value of MCA","(13) - Select wire size based on the value of MCA","(13) - Refer to refrigerant pipe selection or installation manual","(13) - Refer to refrigerant pipe selection or installation manual","(13) - Refer to refrigerant pipe selection or installation manual","(13) - Refer to refrigerant pipe selection or installation manual","(13) - Refer to refrigerant pipe selection or installation manual","(13) - Refer to refrigerant pipe selection or installation manual","(13) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(14) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(14) - Contains fluorinated greenhouse gases","(14) - Contains fluorinated greenhouse gases","(14) - Contains fluorinated greenhouse gases","(14) - Contains fluorinated greenhouse gases","(14) - Contains fluorinated greenhouse gases","(14) - Contains fluorinated greenhouse gases","(14) - Contains fluorinated greenhouse gases"]
["","","","","","(15) - Refer to refrigerant pipe selection or installation manual","(15) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(16) - Contains fluorinated greenhouse gases","(16) - Contains fluorinated greenhouse gases"]