{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":141,"n_cols":23,"rows_kept":141,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXYQQ-U"]
[]
[]
[]
[]
["","","","","","RXYQQ8U7Y1B","RXYQQ10U7Y1B","RXYQQ12U7Y1B","RXYQQ14U7Y1B","RXYQQ16U7Y1B","RXYQQ18U7Y1B","RXYQQ20U7Y1B","RXYQQ22U7Y1B","RXYQQ24U7Y1B","RXYQQ26U7Y1B","RXYQQ28U7Y1B","RXYQQ30U7Y1B","RXYQQ32U7Y1B","RXYQQ34U7Y1B","RXYQQ36U7Y1B","RXYQQ38U7Y1B","RXYQQ40U7Y1B","RXYQQ42U7Y1B"]
["System","Outdoor unit module 1","","","","","","","","","","","RXYQQ10U","RXYQQ8U","RXYQQ12U","RXYQQ12U","RXYQQ12U","RXYQQ16U","RXYQQ16U","RXYQQ16U","RXYQQ8U","RXYQQ10U","RXYQQ10U"]
["","Outdoor unit module 2","","","","","","","","","","","RXYQQ12U","RXYQQ16U","RXYQQ14U","RXYQQ16U","RXYQQ18U","RXYQQ16U","RXYQQ18U","RXYQQ20U","RXYQQ10U","RXYQQ12U","RXYQQ16U"]
["","Outdoor unit module 3","","","","","","","","","","","","","","","","","","","RXYQQ20U","RXYQQ18U","RXYQQ16U"]
["Recommended combination","","","","","4 x FXFQ50BVEB","4 x FXFQ63BVEB","6 x FXFQ50BVEB","1 x FXFQ50BVEB + 5 x FXFQ63BVEB","4 x FXFQ63BVEB + 2 x FXFQ80BVEB","3 x FXFQ50BVEB + 5 x FXFQ63BVEB","2 x FXFQ50BVEB + 6 x FXFQ63BVEB","6 x FXFQ50BVEB + 4 x FXFQ63BVEB","4 x FXFQ50BVEB + 4 x FXFQ63BVEB + 2 x FXFQ80BVEB","7 x FXFQ50BVEB + 5 x FXFQ63BVEB","6 x FXFQ50BVEB + 4 x FXFQ63BVEB + 2 x FXFQ80BVEB","9 x FXFQ50BVEB + 5 x FXFQ63BVEB","8 x FXFQ63BVEB + 4 x FXFQ80BVEB","3 x FXFQ50BVEB + 9 x FXFQ63BVEB + 2 x FXFQ80BVEB","2 x FXFQ50BVEB + 10 x FXFQ63BVEB + 2 x FXFQ80BVEB","6 x FXFQ50BVEB + 10 x FXFQ63BVEB","9 x FXFQ50BVEB + 9 x FXFQ63BVEB","12 x FXFQ63BVEB + 4 x FXFQ80BVEB"]
["Recommended combination 2","","","","","4 x FXSQ50A2VEB","4 x FXSQ63A2VEB","6 x FXSQ50A2VEB","1 x FXSQ50A2VEB + 5 x FXSQ63A2VEB","4 x FXSQ63A2VEB + 2 x FXSQ80A2VEB","3 x FXSQ50A2VEB + 5 x FXSQ63A2VEB","2 x FXSQ50A2VEB + 6 x FXSQ63A2VEB","6 x FXSQ50A2VEB + 4 x FXSQ63A2VEB","4 x FXSQ50A2VEB + 4 x FXSQ63A2VEB + 2 x FXSQ80A2VEB","7 x FXSQ50A2VEB + 5 x FXSQ63A2VEB","6 x FXSQ50A2VEB + 4 x FXSQ63A2VEB + 2 x FXSQ80A2VEB","9 x FXSQ50A2VEB + 5 x FXSQ63A2VEB","8 x FXSQ63A2VEB + 4 x FXSQ80A2VEB","3 x FXSQ50A2VEB + 9 x FXSQ63A2VEB + 2 x FXSQ80A2VEB","2 x FXSQ50A2VEB + 10 x FXSQ63A2VEB + 2 x FXSQ80A2VEB","6 x FXSQ50A2VEB + 10 x FXSQ63A2VEB","9 x FXSQ50A2VEB + 9 x FXSQ63A2VEB","12 x FXSQ63A2VEB + 4 x FXSQ80A2VEB"]
["Recommended combination 3","","","","","4 x FXMQ50P7VEB9","4 x FXMQ63P7VEB9","6 x FXMQ50P7VEB9","1 x FXMQ50P7VEB9 + 5 x FXMQ63P7VEB9","4 x FXMQ63P7VEB9 + 2 x FXMQ80P7VEB9","3 x FXMQ50P7VEB9 + 5 x FXMQ63P7VEB9","2 x FXMQ50P7VEB9 + 6 x FXMQ63P7VEB9","6 x FXMQ50P7VEB9 + 4 x FXMQ63P7VEB9","4 x FXMQ50P7VEB9 + 4 x FXMQ63P7VEB9 + 2 x FXMQ80P7VEB9","7 x FXMQ50P7VEB9 + 5 x FXMQ63P7VEB9","6 x FXMQ50P7VEB9 + 4 x FXMQ63P7VEB9 + 2 x FXMQ80P7VEB9","9 x FXMQ50P7VEB9 + 5 x FXMQ63P7VEB9","8 x FXMQ63P7VEB9 + 4 x FXMQ80P7VEB9","3 x FXMQ50P7VEB9 + 9 x FXMQ63P7VEB9 + 2 x FXMQ80P7VEB9","2 x FXMQ50P7VEB9 + 10 x FXMQ63P7VEB9 + 2 x FXMQ80P7VEB9","6 x FXMQ50P7VEB9 + 10 x FXMQ63P7VEB9","9 x FXMQ50P7VEB9 + 9 x FXMQ63P7VEB9","12 x FXMQ63P7VEB9 + 4 x FXMQ80P7VEB9"]
["Cooling capacity","Prated,c","","","kW","22.4 (1)","28.0 (1)","33.5 (1)","40.0 (1)","45.0 (1)","50.4 (1)","52.0 (1)","61.5 (1)","67.4 (1)","73.5 (1)","78.5 (1)","83.9 (1)","90.0 (1)","95.4 (1)","97.0 (1)","102.4 (1)","111.9 (1)","118.0 (1)"]
["Heating capacity","Prated,h","","","kW","22.4 (2)","28.0 (2)","33.5 (2)","40.0 (2)","45.0 (2)","50.4 (2)","56.0 (2)","61.5 (2)","67.4 (2)","73.5 (2)","78.5 (2)","83.9 (2)","90.0 (2)","95.4 (2)","101.0 (2)","106.4 (2)","111.9 (2)","118.0 (2)"]
["","Nom.","","6°CWB","kW","22.4 (2)","28.0 (2)","33.5 (2)","40.0 (2)","45.0 (2)","50.4 (2)","56.0 (2)","61.5 (2)","67.4 (2)","73.5 (2)","78.5 (2)","83.9 (2)","90.0 (2)","95.4 (2)","101.0 (2)","106.4 (2)","111.9 (2)","118.0 (2)"]
["COP at nom. capacity","6°CWB","","","KW/KW","4.15 (2)","3.69 (2)","3.47 (2)","3.74 (2)","3.59 (2)","3.54 (2)","3.20 (2)","3.57 (2)","3.76 (2)","3.61 (2)","3.54 (2)","3.51 (2)","3.59 (2)","3.56 (2)","3.36 (2)","3.49 (2)","3.56 (2)","3.61 (2)"]
["SEER","","","","","7.6","6.8","6.3","6.3","6.0","6.0","5.9","6.9","6.8","6.7","6.5","6.5","6.4","6.4","6.3","6.9","6.7","6.6"]
["SEER recommended combination 2","","","","","6.9","6.8","5.9","6.3","5.9","6.0","5.9","6.7","6.6","6.5","6.3","6.3","6.3","6.3","6.3","6.8","6.6","6.6"]
["SEER recommended combination 3","","","","","7.5","6.8","6.2","6.2","5.8","6.0","5.9","6.9","6.7","6.6","6.4","6.5","6.2","6.3","6.3","6.9","6.7","6.5"]
["SCOP","","","","","4.3","4.3","4.1","4.0","4.0","4.2","4.0","4.4","4.3","4.2","4.2","4.3","4.2","4.2","4.1","4.3","4.3","4.2"]
["SCOP recommended combination 2","","","","","4.2","4.3","4.1","4.0","4.1","4.2","4.0","4.4","4.3","4.2","4.2","4.3","4.2","4.3","4.2","4.3","4.4","4.3"]
["SCOP recommended combination 3","","","","","4.2","4.1","4.1","4.0","4.0","4.1","3.9","4.3","4.2","4.2","4.2","4.3","4.1","4.2","4.1","4.2","4.3","4.2"]
["Space cooling","A Condition (35°C - 27/19)","","EERd","","3.0","2.3","2.4","2.6","2.1","1.9","1.9","2.6","2.5","2.6","2.3","2.1","2.3","2.1","2.1","2.4","2.2","2.3"]
["","","","Pdc","kW","22.4","28.0","33.5","40.0","45.0","50.4","52.0","61.5","67.4","73.5","78.5","83.9","90.0","95.4","97.0","102.4","111.9","118.0"]
["","B Condition (30°C - 27/19)","","EERd","","5.2","4.7","4.3","4.1","3.9","3.8","3.7","4.8","4.6","4.6","4.4","4.3","4.3","4.2","4.1","4.5","4.5","4.4"]
["","","","Pdc","kW","16.5","20.6","24.7","29.5","33.2","37.1","38.3","45.3","49.7","54.2","57.8","61.8","66.3","70.3","71.5","75.5","82.5","86.9"]
["","C Condition (25°C - 27/19)","","EERd","","9.5","8.3","7.7","7.8","7.7","7.5","7.3","8.5","8.6","8.2","8.1","8.2","8.1","8.1","7.9","8.5","8.3","8.2"]
["","","","Pdc","kW","10.6","13.3","15.9","18.9","21.3","23.9","24.6","29.1","31.9","34.8","37.2","39.7","42.6","45.2","45.9","48.5","53.0","55.9"]
["","D Condition (20°C - 27/19)","","EERd","","18.8","17.0","13.9","14.3","14.2","18.3","18.3","16.0","15.2","14.2","14.3","16.8","14.3","16.8","16.7","17.9","16.0","15.4"]
["","","","Pdc","kW","8.0","9.3","9.4","8.4","9.5","11.5","11.5","18.8","15.8","16.2","16.5","21.0","19.0","20.1","20.4","21.6","23.6","24.8"]
["Space cooling recommended combination 2","A Condition (35°C - 27/19)","","EERd","","2.6","2.4","2.4","2.6","2.1","1.9","1.9","2.6","2.4","2.6","2.3","2.1","2.2","2.1","2.1","2.3","2.2","2.3"]
["","","","Pdc","kW","22.4","28.0","33.5","40.0","45.0","50.4","52.0","61.5","67.4","73.5","78.5","83.9","90.0","95.4","97.0","102.4","111.9","118.0"]
["","B Condition (30°C - 27/19)","","EERd","","4.9","4.7","4.0","4.1","3.8","3.7","3.6","4.6","4.5","4.4","4.3","4.2","4.2","4.2","4.1","4.5","4.4","4.4"]
["","","","Pdc","kW","16.5","20.6","24.7","29.5","33.2","37.1","38.3","45.3","49.7","54.1","57.8","61.8","66.3","70.3","71.5","75.4","82.4","86.9"]
["","C Condition (25°C - 27/19)","","EERd","","8.8","8.5","7.1","7.9","7.6","7.5","7.3","8.2","8.4","7.9","7.8","7.9","8.0","8.1","7.9","8.4","8.1","8.2"]
["","","","Pdc","kW","10.6","13.3","15.9","18.9","21.3","23.9","24.6","29.1","31.9","34.8","37.2","39.7","42.6","45.2","45.9","48.5","53.0","55.9"]
["","D Condition (20°C - 27/19)","","EERd","","15.1","17.2","13.1","14.0","14.0","18.1","18.9","15.6","14.7","13.6","13.8","16.1","14.0","16.5","16.5","17.8","15.9","15.3"]
["","","","Pdc","kW","8.8","9.3","9.1","8.4","9.5","11.4","10.9","18.4","15.4","15.7","16.5","20.5","18.9","20.1","20.4","21.6","23.6","24.8"]
["Space cooling recommended combination 3","A Condition (35°C - 27/19)","","EERd","","3.0","2.3","2.4","2.6","2.1","1.9","1.9","2.5","2.5","2.5","2.3","2.1","2.2","2.1","2.1","2.4","2.2","2.3"]
["","","","Pdc","kW","22.4","28.0","33.5","40.0","45.0","50.4","52.0","61.5","67.4","73.5","78.5","83.9","90.0","95.4","97.0","102.4","111.9","118.0"]
["","B Condition (30°C - 27/19)","","EERd","","5.1","4.7","4.2","4.0","3.7","3.7","3.6","4.8","4.5","4.5","4.3","4.3","4.1","4.1","4.0","4.5","4.4","4.3"]
["","","","Pdc","kW","16.5","20.6","24.7","29.5","33.2","37.1","38.3","45.3","49.7","54.2","57.8","61.8","66.3","70.3","71.5","75.5","82.5","87.0"]
["","C Condition (25°C - 27/19)","","EERd","","9.6","8.4","7.7","7.7","7.4","7.6","7.3","8.5","8.4","8.1","8.0","8.2","7.8","8.0","7.8","8.5","8.4","8.0"]
["","","","Pdc","kW","10.6","13.3","15.9","19.0","21.3","23.9","24.6","29.1","31.9","34.8","37.2","39.7","42.6","45.2","45.9","48.5","53.0","55.9"]
["","D Condition (20°C - 27/19)","","EERd","","16.0","16.9","13.7","14.0","14.1","18.3","18.3","15.8","15.2","14.0","14.1","16.6","13.8","16.6","16.5","17.9","16.1","15.2"]
["","","","Pdc","kW","9.1","9.3","9.4","8.4","9.5","11.6","11.6","18.8","15.7","16.0","16.6","21.0","19.0","20.1","20.4","21.6","23.6","24.8"]
["Space heating (Average climate)","TBivalent","","COPd (declared COP)","","2.5","2.4","2.0","2.3","2.2","1.9","1.8","2.3","2.5","2.3","2.2","2.1","2.4","2.2","2.1","2.2","2.2","2.4"]
["","","","Pdh (declared heating cap)","kW","13.7","16.0","18.4","20.6","23.2","27.9","31.0","34.4","36.9","39.0","41.6","46.3","46.4","51.1","54.2","60.7","62.3","62.4"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","Space heating (Average climate)-=-E condition (-10°C)","","Space heating (Average climate)-=-E condition (-10°C)-=-COPd (declared COP)","","2.5","2.4","2.0","2.3","2.2","1.9","1.8","2.3","2.5","2.3","2.2","2.1","2.4","2.2","2.1","2.2","2.2","2.4"]
["","","","Space heating (Average climate)-=-E condition (-10°C)-=-Pdh (declared heating cap)-=-kW","kW","13.7","16.0","18.4","20.6","23.2","27.9","31.0","34.4","36.9","39.0","41.6","46.3","46.4","51.1","54.2","60.7","62.3","62.4"]
["","TOL","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","2.7","2.6","2.4","2.6","2.6","2.4","2.1","2.6","2.8","2.6","2.6","2.6","2.7","2.6","2.5","2.5","2.6","2.7"]
["","","","Pdh (declared heating cap)","kW","12.1","14.2","16.3","18.2","20.5","24.7","27.4","30.4","32.6","34.5","36.8","41.0","41.0","45.2","47.9","53.7","55.1","55.2"]
["","B Condition (2°C)","","COPd (declared COP)","","3.9","3.9","3.9","3.5","3.5","3.7","3.6","4.0","3.7","3.8","3.8","3.9","3.6","3.7","3.7","3.9","4.0","3.7"]
["","","","Pdh (declared heating cap)","kW","7.4","8.6","9.9","11.1","12.5","15.0","16.7","18.5","19.9","21.0","22.4","24.9","25.0","27.5","29.2","32.7","33.5","33.6"]
["","C Condition (7°C)","","COPd (declared COP)","","6.3","6.4","6.1","6.1","6.3","6.7","6.5","6.3","6.3","6.1","6.2","6.5","6.3","6.5","6.4","6.5","6.5","6.3"]
["","","","Pdh (declared heating cap)","kW","5.0","5.5","6.4","7.1","8.0","9.7","10.7","11.9","13.0","13.5","14.4","16.0","16.1","17.7","18.8","21.3","21.6","21.6"]
["","D Condition (12°C)","","COPd (declared COP)","","7.9","8.2","7.9","8.5","8.6","9.0","9.1","8.2","8.9","8.8","9.0","9.0","9.0","8.8","8.6","8.7","8.7","8.6"]
["","","","Pdh (declared heating cap)","kW","5.9","5.9","6.3","4.9","4.9","7.1","7.1","6.0","5.7","6.0","6.4","7.1","7.1","7.9","8.3","13.1","13.1","9.9"]
["Space heating (Average climate) recommended combination 2","TBivalent","","COPd (declared COP)","","2.4","2.4","1.9","2.3","2.2","1.9","1.8","2.2","2.4","2.2","2.2","2.1","2.4","2.2","2.2","2.3","2.2","2.4"]
["","","","Pdh (declared heating cap)","kW","13.7","16.0","18.4","20.6","23.2","27.9","31.0","34.4","36.9","39.0","41.6","46.3","46.4","51.1","54.2","60.7","62.3","62.4"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.4","2.4","1.9","2.3","2.2","1.9","1.8","2.2","2.4","2.2","2.2","2.1","2.4","2.2","2.2","2.3","2.2","2.4"]
["","","","Pdh (declared heating cap)","kW","13.7","16.0","18.4","20.6","23.2","27.9","31.0","34.4","36.9","39.0","41.6","46.3","46.4","51.1","54.2","60.7","62.3","62.4"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","2.7","2.7","2.4","2.6","2.6","2.4","2.2","2.6","2.7","2.6","2.6","2.6","2.7","2.6","2.5","2.5","2.6","2.7"]
["","","","Pdh (declared heating cap)","kW","12.1","14.2","16.3","18.2","20.5","24.7","27.4","30.4","32.6","34.5","36.8","41.0","41.0","45.2","47.9","53.7","55.1","55.2"]
["","B Condition (2°C)","","COPd (declared COP)","","3.9","4.0","3.9","3.5","3.5","3.8","3.7","4.1","3.7","3.8","3.8","3.9","3.6","3.8","3.7","3.9","4.0","3.7"]
["","","","Pdh (declared heating cap)","kW","7.4","8.6","9.9","11.1","12.2","15.0","16.7","18.5","19.9","21.0","22.4","24.9","25.0","27.5","29.2","32.7","33.5","33.6"]
["","C Condition (7°C)","","COPd (declared COP)","","6.3","6.5","6.1","6.1","6.3","6.8","6.5","6.3","6.3","6.1","6.3","6.6","6.3","6.6","6.5","6.5","6.5","6.4"]
["","","","Pdh (declared heating cap)","kW","5.0","5.5","6.4","7.1","8.0","9.7","10.7","11.9","13.1","13.1","14.4","16.0","16.1","17.7","18.8","21.3","21.6","21.6"]
["","D Condition (12°C)","","COPd (declared COP)","","7.8","8.3","7.9","8.6","8.7","9.1","9.2","8.4","9.0","8.9","9.1","9.1","9.1","8.9","8.8","8.8","8.8","8.7"]
["","","","Pdh (declared heating cap)","kW","5.9","6.0","6.4","4.9","5.0","7.2","7.2","6.0","5.7","6.0","6.4","7.2","7.1","7.9","8.3","13.2","13.2","10.0"]
["Space heating (Average climate) recommended combination 3","TBivalent","","COPd (declared COP)","","2.5","2.4","2.0","2.3","2.2","1.9","1.8","2.3","2.4","2.2","2.2","2.1","2.4","2.2","2.1","2.2","2.2","2.4"]
["","","","Pdh (declared heating cap)","kW","13.7","16.0","18.4","20.6","23.2","27.9","31.0","34.4","36.9","39.0","41.6","46.3","46.4","51.1","54.2","60.7","62.3","62.4"]
["","","","Tbiv (bivalent temperature)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","TOL","","COPd (declared COP)","","2.5","2.4","2.0","2.3","2.2","1.9","1.8","2.3","2.4","2.2","2.2","2.1","2.4","2.2","2.1","2.2","2.2","2.4"]
["","","","Pdh (declared heating cap)","kW","13.7","16.0","18.4","20.6","23.2","27.9","31.0","34.4","36.9","39.0","41.6","46.3","46.4","51.1","54.2","60.7","62.3","62.4"]
["","","","Tol (temperature operating limit)","°C","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","A Condition (-7°C)","","COPd (declared COP)","","2.7","2.6","2.4","2.6","2.6","2.4","2.1","2.6","2.7","2.6","2.6","2.5","2.7","2.6","2.4","2.5","2.6","2.7"]
["","","","Pdh (declared heating cap)","kW","12.1","14.2","16.3","18.2","20.5","24.7","27.4","30.4","32.6","34.5","36.8","41.0","41.0","45.2","47.9","53.7","55.1","55.2"]
["","B Condition (2°C)","","COPd (declared COP)","","3.9","3.7","3.9","3.5","3.5","3.7","3.6","4.0","3.7","3.8","3.8","3.9","3.6","3.7","3.6","3.8","3.9","3.7"]
["","","","Pdh (declared heating cap)","kW","7.4","8.6","9.9","11.1","12.5","15.0","16.7","18.5","19.9","21.0","22.4","24.9","25.0","27.5","29.2","32.7","33.5","33.6"]
["","C Condition (7°C)","","COPd (declared COP)","","6.2","6.4","6.0","6.1","6.2","6.5","6.3","6.2","6.3","6.1","6.2","6.3","6.3","6.4","6.3","6.3","6.4","6.3"]
["","","","Pdh (declared heating cap)","kW","4.9","5.5","6.4","7.1","8.0","9.7","10.7","11.9","12.9","13.5","14.4","16.0","16.1","17.7","18.8","21.2","21.6","21.6"]
["","D Condition (12°C)","","COPd (declared COP)","","7.8","8.1","7.8","8.5","8.6","8.7","8.7","8.2","8.9","8.8","9.0","8.6","9.0","8.9","8.3","8.5","8.4","8.6"]
["","","","Pdh (declared heating cap)","kW","5.8","5.9","6.2","4.9","4.9","6.9","6.9","6.0","5.7","6.0","6.4","7.1","7.1","7.9","8.3","12.9","12.8","9.9"]
["Capacity range","HP","","","","8","10","12","14","16","18","20","22","24","26","28","30","32","34","36","38","40","42"]
["Maximum number of connectable indoor units","","","","","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)"]
["Indoor index connection","Min.","","","","100.0","125.0","150.0","175.0","200.0","225.0","250.0","275.0","300.0","325.0","350.0","375.0","400.0","425.0","450.0","475.0","500.0","525.0"]
["","Max.","","","","260.0","325.0","390.0","455.0","520.0","585.0","650.0","715.0","780.0","845.0","910.0","975.0","1040.0","1105.0","1170.0","1235.0","1300.0","1365.0"]
["Dimensions","Unit","","Height","mm","1685","1685","1685","1685","1685","1685","1685"]
["","","","Width","mm","930","930","930","1240","1240","1240","1240"]
["","","","Depth","mm","765","765","765","765","765","765","765"]
["Weight","Unit","","","kg","195","195","195","276","276","310","310"]
["Fan","External static pressure","","Max.","Pa","78","78","78","78","78","78","78"]
["Compressor","Type","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5.0","-5.0","-5.0","-5.0","-5.0","-5.0","-5.0"]
["","","","Max.","°CDB","43.0","43.0","43.0","43.0","43.0","43.0","43.0"]
["","Heating","","Min.","°CWB","-20.0","-20.0","-20.0","-20.0","-20.0","-20.0","-20.0"]
["","","","Max.","°CWB","15.5","15.5","15.5","15.5","15.5","15.5","15.5"]
["Sound power level","Cooling","","Nom.","dBA","78.0 (4)","79.1 (4)","83.4 (4)","80.9 (4)","85.6 (4)","83.8 (4)","87.9 (4)","84.8 (4)","86.3 (4)","85.3 (4)","87.6 (4)","86.6 (4)","88.6 (4)","87.8 (4)","89.9 (4)","88.8 (4)","87.3 (4)","89.1 (4)"]
["Sound pressure level","Cooling","","Nom.","dBA","57.0 (5)","57.0 (5)","61.0 (5)","60.0 (5)","63.0 (5)","62.0 (5)","65.0 (5)","62.5 (5)","64.0 (5)","63.5 (5)","65.1 (5)","64.5 (5)","66.0 (5)","65.5 (5)","67.1 (5)","66.2 (5)","65.2 (5)","66.5 (5)"]
["Refrigerant","Type","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["","GWP","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","tCO2Eq","12.3","12.5","13.2","21.5","23.6","24.4","24.6"]
["","Charge","","","kg","5.9","6.0","6.3","10.3","11.3","11.7","11.8"]
["Piping connections","Liquid","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","9.52","9.52","12.7","12.7","12.7","15.9","15.9","15.9","15.9","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1"]
["","Gas","","Type","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","","","OD","mm","19.1","22.2","28.6","28.6","28.6","28.6","28.6","28.6","34.9","34.9","34.9","34.9","34.9","34.9","41.3","41.3","41.3","41.3"]
["","Total piping length","System","Actual","m","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)","300 (6)"]
["Standard Accessories","Installation manual","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Operation manual","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Connection pipes","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["Power supply","Name","","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Phase","","","","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~"]
["","Frequency","","","Hz","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Notes","","","","","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)"]
["","","","","","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(7) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(8) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(9) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(10) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan","(11) - FLA means the nominal running current of the fan"]
["","","","","","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%.","(12) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(13) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(14) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )"]
["","","","","","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(15) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality"]
["","","","","","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room.","(16) - Sound values are measured in a semi-anechoic room."]
["","","","","","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(17) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA"]
["","","","","","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(18) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power","(19) - Ssc: Short-circuit power"]
["","","","","","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual","(20) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(21) - Multi combination (22~54HP) data is corresponding with the standard multi combination"]